****

THERMAL INSULATION

SECTION 07 21 19

Foamed-in-Place Insulation

**ICYNENE® HFO 200**

This specification utilizes the Construction Specifications Institute’s (CSI) 3-Part formatting. The specification is a manufacturer-specific product specification to be used by design professionals as a guide specification. Editing notes are indicated in *red italics* and precede specification text. Delete editing notes in final specification.

This specification specifies medium density spray foam insulation by HUNTSMAN BUILDING SOLUTIONS. Revise section number and title below to suit project requirements.

The specified product may contribute to the following credits/points for the respective rating system:

LEED V.4.1

National Green Building Standard (NGBS, ICC-700)

ERI (Energy Rating Index)

1. **GENERAL**
	1. **SECTION INCLUDES**

*\*\* NOTE TO SPECIFIER \*\* Delete items below not required for project.*

* + 1. Spray-in-place rigid closed cell 2-pound polyurethane foam insulation in various

 assemblies, to provide an air barrier and improved thermal resistance.

* 1. **RELATED SECTIONS**

*\*\* NOTE TO SPECIFIER \*\* Delete any sections below not relevant to this project; add others as required.*

* + 1. Section 03 30 00 - Cast in Place Concrete.
		2. Section 03 40 00 - Structural Pre-cast Concrete.
		3. Section 04 20 00 - Unit Masonry.
		4. Section 05 30 00 - Metal Decking.
		5. Section 05 40 00 - Cold Formed Metal Framing.
		6. Section 06 10 00 - Rough Carpentry.
		7. Section 07 10 00 - Waterproofing.
		8. Section 07 26 00 - Vapor Barrier.
		9. Section 07 40 00 - Preformed Roofing and Cladding/Siding.
		10. Section 07 65 00 - Flexible Flashing.
		11. Section 07 80 00 – Fire protection.
		12. Section 07 81 00 - Applied Fireproofing.
		13. Section 09 20 00 - Gypsum Board.
		14. Section 09 22 00 - Metal Support Systems.
	1. **REFERENCES**

*\*\* NOTE TO SPECIFIER \*\* Delete references from the list below that are not actually required by the text of the edited section.*

* + 1. American Society for Testing and Materials (ASTM):
			1. ASTM C518 Standard Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus
			2. ASTM C1029 Standard Specification for Spray-Applied Rigid Cellular Polyurethane Thermal Insulation
			3. ASTM C1338 Standard Test Method for Determining Fungi Resistance of Insulation Materials and Facings
			4. ASTM D1621 Standard Test Method for Compressive Properties of Rigid Cellular Plastics
			5. ASTM D1622 Standard Test Method for Apparent Density of Rigid Cellular Plastics
			6. ASTM D1623 Standard Test Method for Tensile and Tensile Adhesion Properties of Rigid Cellular Plastics
			7. ASTM D2126 Standard Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging
			8. ASTM D2842 Standard Test Method for Water Absorption of Rigid Cellular Plastics
			9. ASTM D2856 Standard Test Method for Open-Cell Content of Rigid Cellular Plastics by the Air Pycnometer
			10. ASTM E84 Standard Test Method for Surface Burning Characteristics of Building Materials
			11. ASTM E96 Standard Test Methods for Water Vapor Transmission of Materials
			12. ASTM E283 Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Skylights, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen
			13. ASTM E2178 Standard Test Method for Determining Air Leakage Rate and Calculation of Air Permeance of Building Materials
		2. Other standards:
			1. AC71 Foam Plastic Sheathing Panels Used as Weather-resistive Barriers
			2. AC377 Acceptance Criteria for Spray-Applied Foam Plastic Insulation
		3. National Fire Protection Association (NFPA):
			1. NFPA 285 Standard Fire Test Method for Evaluation of Fire Propagation Characteristics of Exterior Wall Assemblies Containing Combustible Components
			2. NFPA 286 Standard Methods of Fire Tests for Evaluating Contribution of Wall and Ceiling Interior Finish to Room Fire Growth
		4. International Code Council – International Residential Code:
			1. Section R104.11 Alternate materials, design and methods of construction and equipment.
			2. Section R316 Foam Plastic Insulation.
			3. Section 806.5 Unvented attic and unvented enclosed rafter assemblies.
		5. International Code Council – International Building Code:
			1. Section 104.11 Alternative materials, design and methods of construction and

 equipment.

* + - 1. Section 1203.3 Unvented attic and unvented enclosed rafter assemblies
			2. Section 2603 Foam Plastic Insulation.
	1. **SUBMITTALS**
		1. Submit under provisions of Section 01 30 00.
		2. Before commencing work, submit in accordance with local code.
			1. Submit technical data sheets and samples as required by local code officials.
			2. Submit the technical data sheet from the manufacturer showing the test results

 from the ASTM E84 (Surface Burning Characteristics).

* + - 1. Submit AC377 Appendix X compliance.
		1. Product Data: Manufacturer's data sheets on each product to be used, including:
			1. Preparation instructions and recommendations.
			2. Storage and handling requirements and recommendations.
			3. Installation methods.
	1. **QUALITY ASSURANCE**
		1. Installer Qualifications:
			1. Contractor performing work under this section shall be authorized by Huntsman Building Solutions in the art of applying spray polyurethane foam insulation.
			2. Provide current HUNTSMAN BUILDING SOLUTIONS Authorized Contractor

Certificate.

*\*\* NOTE TO SPECIFIER \*\* Include a mock-up if the project size and/or quality warrant taking such a precaution. The following is one example of how a mock-up on a large project might be specified. When deciding on the extent of the mock-up, consider all the major different types of work on the project.*

* + 1. Mock-Up: Provide a mock-up for evaluation of surface preparation techniques and

 application workmanship.

* + - 1. Finish areas designated by Architect.
			2. Do not proceed with remaining work until installation is approved by Architect.
			3. Rework mock-up area as required to produce acceptable work.
	1. **DELIVERY, STORAGE, AND HANDLING**
		1. Materials shall be delivered in manufacturer’s original containers clearly labelled

 with manufacturer’s name, product identification, safety information, net weight of

 contents and expiration date.

* + 1. Material shall be stored in a safe manner and where the temperatures are in the

 limits specified by the material manufacturer.

* + 1. Empty containers shall be removed from site on a daily basis.
		2. Store and dispose of solvent-based materials, and materials used with solvent-

 based materials, in accordance with requirements of local authorities having

 jurisdiction.

* 1. **PROJECT CONDITIONS**
		1. Maintain environmental conditions (temperature, humidity, and ventilation) within

 limits recommended by manufacturer for optimum results. Do not install products

 under environmental conditions outside manufacturer's absolute limits.

* + 1. Ventilate insulation application area in accordance with the Spray Foam Coalition’s

 Guidance on best practices for the installation of Spray Polyurethane Foam.

* + 1. Protect workers as recommended by the Spray Foam Coalition’s Guidance on best

 practices for the installation of Spray Polyurethane Foam.

* + 1. Protect adjacent surfaces, windows, equipment and site areas from damage of overspray.
	1. **WARRANTY**
		1. Manufacturer’s Warranty: HUNTSMAN BUILDING SOLUTIONS warrants spray-in-

 place urethane foam insulation, when installed by certified contractors using factory-

 trained applicators and applied in accordance with the Installation Instructions, will

 perform as stated in the Product Technical Data Sheet.

* + - 1. This warranty is in effect throughout the life of the building provided the original purchaser registers with the Warranty Department of the Manufacturer within thirty days of occupancy.
			2. Manufacturer’s sole responsibility under this Limited Lifetime Warranty shall be to repair or replace any defective Product at the cost of the material only.
			3. Manufacturer shall not be responsible for labor cost or any other costs whatsoever related to, or in connection with the removal or installation of either the original or replacement product.
			4. Refer to [www.huntsmanbuildingsolutions.com](http://www.huntsmanbuildingsolutions.com) for full warranty terms.
1. **PRODUCTS**
	1. **ENVIRONNEMENTAL REQUIREMENTS**
		1. The product shall have a product specific Environmental Product Declaration (EPD).
		2. The product shall have a minimum of 19% of recycled content.
		3. The product shall have a minimum of 6% of renewable content.
		4. The product shall be UL Greenguard Gold certified.
	2. **MANUFACTURERS**
		1. Acceptable Manufacturer: HUNTSMAN BUILDING SOLUTIONS

3315 East Division Street, Arlington, TX 76011

(855) 742-7227

architect@huntsmanbuilds.com

<http://www.huntsmanbuildingsolutions.com>

*\*\* NOTE TO SPECIFIER \*\* Delete two of the following three paragraphs: coordinate with requirements of Division 1 section on product options and substitutions.*

* + 1. Substitutions: Equivalent as judged by Architect
			1. Contact HUNTSMAN BUILDING SOLUTIONS Building Science and Engineering Department for product comparison data
				1. (855) 942-7273
				2. architect@huntsmanbuilds.com
		2. Requests for substitutions will be considered in accordance with provisions of

Section 01600.

* 1. **SPRAY FOAM INSULATION**
		1. Spray Applied Rigid Polyurethane Foam Insulation System: ICYNENE® HFO 200
			1. Manufacturer: HUNTSMAN BUILDING SOLUTIONS, Arlington, TX
			2. Product Approval:
				1. IAPMO Uniform Evaluation Service Report 926.
				2. Approved for use in building types I, II, III, IV, and V construction under IBC and dwellings for IRC.
				3. AC377 Appendix X compliant.
			3. Application Options:
				1. Application with a prescriptive Thermal Barrier:

There is no thickness limit when installed in floors or ceilings behind 1/2 inch gypsum wall board or equivalent 15 minute thermal barrier in accordance with IBC 2603.4 or IRC R316.4.

* + - * 1. Application without a prescriptive Thermal Barrier:

Up to 11-1/2 inches (292 mm) on the underside of the roof sheathing or in floor assemblies and 7-1/2 inches (191 mm) on vertical surfaces with:

A minimum of 18 wet mils (12 dry mils) of DC-315 intumescent coating

Up to 9-1/2 inches (241 mm) on the underside of the roof sheathing or in floor assemblies and 6-1/2 inches (165 mm) on vertical surfaces with:

A minimum of 16 wet mils (11 dry mils) of No-Burn Plus ThB intumescent coating

* + - * 1. Attics and Crawlspaces: AC 377 Appendix X compliant (Entry to the attic or crawlspace is only to service utilities and NO storage is permitted). Minimum application thickness of 1 inch.

Up to 11-1/2 inches (292 mm) on the underside of the roof sheathing or in floor assemblies and 7-1/2 inches (191 mm) on vertical surfaces, the insulation may be left exposed without a thermal barrier, ignition barrier or intumescent coating

* + - * 1. Use on Attic Floors:

Up to 11-1/2 inches (292mm) between and over the joists in attic floors

* + - * 1. Use as a Vapor Retarder: Class II vapor retarder @ < 1.0 perm, ICYNENE® HFO 200 minimum thickness of 1.0 inches.
			1. Physical Properties:

|  |  |  |
| --- | --- | --- |
| Density | ASTM D1622 | 2.0 – 2.4 lb/ft³ |
| Thermal Resistance  | ASTM C518 | 1’’ = R-7.43.5’’ = R-23 |
| Dimensional Stability    | ASTM D2126(% of change in volume at 28 days)158°F (70°C) 97% R.H. | -3.7 % |
| Surface burning characteristics | ASTM E84 | Class 1 |
| Flame spread index | ASTM E84 | 12 |
| Smoke development | ASTM E84 | 350 - 400 |
| Air Permeance | ASTM E2178at 75 Pa at 1’’ | <0.02 L/s· m² |
| Air Permeance | ASTM E283at 75 Pa at 1’’ | <0.02 L/s· m² |
| Water Absorption | ASTM D2842 | 0.3% |
| Water vapor permeance  | ASTM E96 at 1’’Class II Vapor Retarder | 0.91 perms |
| Compressive Strength | ASTM D1621 | 31 psi |
| Tensile Strength | ASTM D1623 | 44 psi |
| Fungi Resistance | ASTM C1338 | No fungal growth |
| Closed Cell Content | ASTM D2856 | 98% |
| Standard Specification for spray applied rigid cellular polyurethane thermal insulation | ASTM C1029 | Type II Compliant |
| Commercial Fire Resistance | NFPA 285 | Assembly passed |

* 1. **ACCESSORY PRODUCTS**
		1. Water Based Intumescing coatings:
			1. Product: DC315, Manufactured by International Fireproof Technology, Inc.
			2. Product: No-Burn Plus ThB, Manufactured by No-Burn, Inc.
		2. Primers:
			1. Product: Adbond manufactured by Adfast or Thermo-Prime by HUNTSMAN

 BUILDING SOLUTIONS

* + - * 1. Application: Follow manufacturer’s application recommendations.
				2. Recommended for oily surfaces and galvanized steel like Z-bar, PVC, curtain walls and steel decks
1. **EXECUTION**
	1. **EXAMINATION**
		1. Do not begin installation until substrates have been properly prepared.
		2. If substrate preparation is the responsibility of another installer, notify General

 Contractor, Architect or other point of contact of unsatisfactory preparation before

 proceeding.

* + 1. Commencement of work outlined in this section shall be deemed as acceptance of

 existing work and conditions.

* 1. **PREPARATION**
		1. Clean surfaces thoroughly prior to installation.
		2. Apply only when surfaces and environmental conditions are within limits prescribed

 by the material manufacturer.

* + 1. Prepare surfaces using the methods recommended by the manufacturer for

 achieving the best result for the substrate under the project conditions.

* + 1. It is recommended to install primer on oily surfaces and galvanized steel
	1. **INSTALLATION**
		1. Install in accordance with manufacturer's instructions.
		2. Apply as recommended by manufacturer to thickness as indicated on drawings.
		3. Equipment used to apply the foam insulation shall have fixed ratio positive

 displacement pumps approved by foam manufacturer.

* 1. **PROTECTION**
		1. Protect installed products until completion of project.
		2. Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION 07 21 19